POLICY DOCUMENT

Electrical Policy

| POLICY TITLE: | Electrical Policy |
| --- | --- |
| LEAD OFFICER: | Electrical Compliance Officer |
| DATE APPROVED: |  |
| APPROVED BY: | Executive Management Team |
| IMPLEMENTATION DATE: | April 2026 |
| DATE FOR NEXT REVIEW: | April 2029 |
| ADDITIONAL GUIDANCE: | Repairs & Maintenance Policy Tenant Health & Safety Policy Decant Policy No Access Policy Vulnerable Persons Policy |
| TEAMS AFFECTED: | Repairs and Maintenance Services Caretakers Procurement Health and Safety Asset Management Access Team Housing Management Anti-Social Behaviour Team |
| THIS POLICY REPLACES: | Electrical Policy V3 July 2023 |

Brief Policy Summary: This policy sets out the organisations approach towards managing the electrical installations within SLHD’s premises.

# Document Control

Revision History

| Date of this revision: | January 2026 |
| --- | --- |
| Date of next review: | April 2029 |
| Responsible Officer: | Electrical Compliance Officer |

| Version Number | Version Date | Author/Group commenting | Summary of Changes |
| --- | --- | --- | --- |
| 0.1 | 17/07/2017 | Mechanical and Electrical Service Manager | This is a new policy. And therefore has nothing to replace, and no track changes |
| 1.0 | August 2017 | EMT | Approved |
| 1.1 | 17/06/2020 | EMT/Board | Review of policy, new 18th Edition Electrical wiring regulations, decisions made by SLHD to replace PVC consumer unit with metal ones and to introduce additional protection within the consumer units installed in our high rise properties, Milton Court and Jubilee court, as these will have Arc Fault detection Devices (AFDD) and surge protection. |
| 2.0 | 23/06/2020 | EMT | Approved by EMT |
| 2.1 | January 2023 | Electrical Compliance Officer / Electrical Team | - Add the role of the Electrical Compliance Officer - Add the use of C365 - To add AFDDs to 32A socket circuits and 20A Distribution circuits supplying out-house buildings on domestic rewires. - Installation of Type 2 SPDs on new smoke alarm circuits - The taking of pictures before and after an Electrical Test |
| 3.0 | April 2023 | EMT | Approved by EMT |
| 3.1 | January 2026 | Electrical Compliance Officer | - Update Policy Principles in line with new Social Rented Sector Regulations 2025 - Add definitions of Remedial Coding - Add definitions of Annual Servicing and Checks - Emergency Procedures |
| 4.0 | April 2026 | EMT | Approved EMT |

# Policy Creation and Review Checklist

| Action | Responsible Officer | Date Completed |
| --- | --- | --- |
| Best practice researched (Housemark, HQN, Audit Commission, general websites) | Mechanical and Electrical Service Manager | June 2020 |
| Review current practices from similar organisations | Mechanical and Electrical Service Manager | June 2020 |
| Review customer satisfaction data from the area the policy relates to | Mechanical and Electrical Service Manager | June 2020 |
| Review Customer complaints from the area the policy relates to | Mechanical and Electrical Service Manager | June 2020 |
| Undertake customer consultation if applicable | N/A |  |
| Staff consultation if applicable | N/A |  |
| Trade Union consultation if applicable | N/A |  |
| Stakeholder consultation if applicable | N/A |  |
| Equality analysis carried out | Mechanical and Electrical Service Manager | June 2020 |

NB. The above table must be completed on all occasions. The policy will not be accepted or approved by EMT without this information completed.

CONTENTS

1.	Introduction										   5

2.	Purpose										   5

3.	Scope											   6

4.	Responsibilities		                                                                               6

5.	Policy Principles									   10

6.	Consultation										   13

7.	Monitoring & Review								   13

8. 	Emergency Procedure                                                                                      14

9.        Performance Standards                                                                                    14

10.      Partnership Issues 		                                                                               14

11.	Appendix 1                                                                                                        15

# 1.    Introduction

1.1	This policy applies to all common/communal areas, general needs and supported housing properties owned or managed by St Leger Homes Doncaster (SLHD). This document outlines the standards required for safety in respect of the installation, repairs and testing of electrical apparatus within our properties to minimise risk and ensure adequate control measures are in place.

# 2.    Purpose

2.1	SLHD is committed to the safety of its tenants, employees and the external service providers (ESP). Electricity can kill or severely injure people and cause damage to property, and every year many accidents involving electric shock or burns are reported to the Health and Safety Executive (HSE). Most of the fatal incidents are caused by contact with overhead power lines; however, non-fatal shocks can cause severe and permanent injury.

The main hazards are:

• Contact with live parts (often at normal mains voltage);

• Faults leading to a fire; and

• Fire or explosion where electricity was the source of ignition in a flammable

atmosphere.

This can occur through:

• The electrical installation and equipment deteriorating over time;

• Damage to switches, sockets and other equipment (possibly through

vandalism);

• Misuse of the installation and equipment; and

• Poor maintenance of the installation.

2.2	SLHD will ensure the provision of a safe working environment in respect of all its electrical installations, apparatus and equipment. This will be achieved by setting standards based on statutory requirements and present good practice, interpreted by persons competent to do so. No person is allowed to plan, order, install, repair, replace, maintain design or decommission ANY electrical system or part unless competent to do so.

2.3	SLHD has set standards of competence for individuals to deliver a safe working environment. A competent person is defined as someone who has the relevant skills, knowledge, training and experience. Electricians employed by SLHD are qualified to Electrical NVQ Level 3 and trained to the latest Edition of the IEE Wiring Regulations (BS7671), including City and Guilds 2382, with a requirement for continuous professional development (CPD. Our external contractors must also meet this same standard.

2.4	In this section, the use of the words ‘electrical system’ and ‘electrical equipment or apparatus’ includes fire alarm systems, emergency lighting and security systems (closed circuit television, intruder alarms, mains powered doorbells). This list is not exhaustive.

NOTE: The Electricity at Work Regulations 1989 define ‘electrical equipment’ as anything used, intended to be used or installed for use to generate, provide, transmit, transform, rectify, convert, conduct, distribute, control, store, measure or use electrical energy.

# Scope

# 3.1   This policy is applicable to all properties under the management of SLHD, domestic rented properties, domestic housing stock, private landlords and commercial responsibilities, and all work undertaken in these properties on CDC’s (City of Doncaster Council) behalf.

# 3.2   This policy will apply to all SLHD employees and contractors undertaking electrical work on SLHD behalf and anyone likely to be put at risk from work on those properties.

# 3.3   The specifications as compiled will include the General Health and Safety Policy, along with relevant working procedures of SLHD.

# Responsibilities

# 4.1	EMT

# The Chief Executive retains all responsibility of the stock managed by SLHD and ensuring that they are compliant.

# 4.2   Leadership Team

# One of the Executive Management Teams duties is to ensure a member of the Executive Management Team has a responsibility to provide sufficient resources for the health, safety and compliance function to be effectively carried out.

# Heads of Service shall ensure the implementation of suitable health and safety arrangements and provide sufficient resources within their service area in order to comply with this Policy and relevant Health and Safety Legislation.

# This will include the provision of sufficient instruction, training and supervision to SLHD staff carrying out electrical work and other employees who use electrical appliances to ensure compliance with this procedure.

# The Leadership Team will designate Building Managers who have the management responsibility for ensuring that the relevant checks and maintenance of the electrical systems have been carried out and that records are kept in accordance with retention and Health and Safety policies. This includes office premises or sites occupied by SLHD employees, communal areas in flats, communal halls and community centres and shops.

# For electrical checks within individual tenanted properties this responsibility lies with the Mechanical and Electrical Service Manager, with the support of the housing management team to seek access through the courts where the tenant refuses access.

# 4.3	Electrical Duty Holder

# The Electrical Duty Holder is appointed by the Leadership Team and is responsible for interpreting relevant legislation and standards and defining the standards and procedures that ensure SLHD compliance with such regulations. The Duty Holder on behalf of SLHD is the Mechanical and Electrical Service Manager. They are responsible for maintaining and monitoring the standard of electrical work undertaken to ensure it complies with legislation, including having fixed, and portable electrical items covered by an examination schedule with records kept. They must also ensure that all persons working on electrical systems are competent to do so, that adequate isolation and permit procedures are in place, and that records are kept of work including installation work.

# The Electrical Duty Holder will be the point of contact for NICEIC and must ensure that all design and installation work in SLHD properties comply with the current guidance and legislation including the Electricity at Work Regulations 1989.

# SLHD will actively participate in the Electrical Safety Standards Advisory Group (ESSAG) arranged by CDC. A SLHD representative (the SLHD Mechanical and Electrical Service Manager or a nominated representative) will attend the ESSAG meetings as a means of engaging in discussion of best practice, changes of legislation and other relevant matters and report back and disseminate the information as required to SLHD staff.

# 4.4 	Building Managers

# SLHD has a number of designated Building Managers who are responsible for carrying out health and safety inspections on the building/premises or site for which they are responsible.

# In respect of this policy Building Managers shall liaise with the Facilities Management Officer to ensure that electrical safety standards have been implemented and met at the office based sites for which they are responsible, including the statutory inspection and testing of electrical items. For all other sites liaison will take place with the Mechanical and Electrical Service Manager.

Building Managers must ensure formal visual inspections of electrical items take place, are recorded, and ensure defects are reported to the Facilities Management Officer or the Mechanical and Electrical Manager, depending on the site. Building Managers must ensure that distribution boards are clearly marked and access is restricted to authorised persons only.

Building Managers must regularly inspect the workplace they are responsible for and complete a periodic inspection report, and a 6 monthly test of the Residual Current Device (RCD) with the consumer unit or units is carried out and recorded. All portable and fixed electrical appliances and installations in their area of responsibility must be inspected and tested, and all faulty items taken out of service. It is the responsibility of Building manager to ensure that all electrical items are Electrical Equipment Testing (EET) formally known as Portable Appliance Tested (PA Tested) within the specific time frame. See Appendix 1 on page 15 for guidance.

4.5	Qualifying Supervisors

# The Electrical Team Leaders and other nominated employees that are qualified to carry out NICEIC assessments to all the electricians employed by SLHD.

# This includes checking all electrical certificates (EICR) completed by the SLHD electrician, updating the electrician on any electrical regulation changes and on-site inspections on voids and planned electrical works.

# 4.6 	Team Leaders and Line Managers

# Team Leaders and Line Managers must ensure the safety of their teams in relation to electrical equipment by ensuring visual checks are carried out by users on portable equipment, and all examination schedules are adhered to. They must remove from use any defective or damaged equipment that is identified and arrange for its repair or disposal.

# It is the responsibility of Team Leaders and Line managers to ensure that all electrical items have a valid EET within the specific time frame.

# 4.7 	Electrical Compliance Officer

# The Electrical Compliance Officer is responsible for maintaining the standards of Electrical works undertaken by SLHD and all contractors working on behalf of SLHD.

# The role of the Electrical Compliance Officer is to offer guidance in relation to electrical installations or regulations and make sure all properties or buildings have a valid in date certificate.

The Electrical Compliance Officer will input the certificates onto C365 system. While uploading onto C365 the Electrical Compliance Officer will check the certificates ensuring they are complete and compliant;

- If the certificate is a paper copy certificate - The Electrical Compliance Officer will check the certificate and then scan and then upload onto C365.

# If Electronic Certificate – the Electrical Compliance Officer will download the certificate off of the relevant system, check the certificate and then upload onto C365.

# Work with our External Auditors and conduct an agreed percentage of external / internal electrical works over the 5 year electrical programme. Liaising with the contractors and the consultants to arrange corrections / re calls / Improvement registers etc

# 4.8 	Health, Safety & Compliance Team

# The Health and Safety Team shall provide support and advice to all levels in the organisation with respect to Safety Standards.

# 4.9 	Procurement Team of City of Doncaster Council (CDC).

# CDC will support SLHD with all tenders involving electrical work to ensure ESP (External Service Provider) who are engaged to undertake electrical work are competent to do so.

# 4.10 Housing Management

Area Teams and the Access Team support EICR access enforcement by arranging appointments (after no access), issuing reminders, and escalating no-access cases. Their work helps ensure Electricians can enter properties on time so electrical safety checks stay compliant.

# 4.11 	Employees

# The Electricity at Work Regulations 1989 require that any electrical equipment that has the potential to cause injury is maintained in a safe condition. However, the Regulations do not specify what needs to be done, by whom or how frequently. The regulations don't make inspection or testing of electrical appliances a legal requirement, nor do they make it a legal requirement to undertake this annually. The frequency of inspection and testing depends upon the type of equipment and the environment it is used in Appendix 1 details the requirements.

# Employees must comply with these requirements in Appendix 1 and visually inspect any appliance before use. If any defect or fault is found the item must be removed from use and it must be reported to their line manager immediately. Tools and equipment that belong to SLHD shall have EET and taken out of use if it fails this test. No employee must alter or work on an electrical appliance unless suitably trained and competent to do so.

# Employees must ensure that no electrical apparatus is brought for use in SLHD premises or for work activities unless approved by their line manager and it has been inspected and deemed safe to use.

4.11 External Auditors

As well as internal auditing, SLHD will be using external auditors to undertake work in progress audits, and post visit audits on a rotation basis to ensure that all audits are kept impartial and fair. Further information can be found in the Elec Quality Control (QC) Procedure.

# Policy Principles

# 5.1 	As responsible social landlords, SLHD will minimize the risks associated with electrical safety and ensure that all our electrical safety duties are carried out. SLHD will:

# Work to the latest version of the IET Wiring Regulations BS7671.

# Replacement of PVC consumer units with metal consumer units at void stage.

# SLHD will carry out a 5 year Domestic and Non-Domestic Electrical Installation Condition Report (EICR) programme in line with electrical Regulations and The Social Rented Sector Regulations 2025;. Remedial work identified as part of the EICR must be completed within timescales.

# Ensure that all electrical tasks are undertaken on a system with no live load and safe electrical isolation has taken place along with locking off;

# Ensure that all electrical installations are tested and certified prior to letting and a copy of the EICR provided to the customer in line with current legislation;

# Use NICEIC (National Inspection Council for Electrical Installation Contracting) or equivalent contractors;

# Give relevant staff appropriate electrical training;

# Undertake regular audits;

# To upload and maintain all documentation and certificates are compliant and uploaded onto the relevant system(s)

# Maintain a clear policy and set of procedures, to be reviewed every three years

# Full rewires or partial rewires to properties will be carried out as and when the wiring is identified as past economical repair on the EICR.

# 5.2	Electrical Testing and Remedials

# SLHD will ensure that all tenanted homes and non-domestic buildings have a valid 5 year EICR unless the competent person recommends this to be done sooner or upon commencement of a new tenancy or following planned component replacement works. These will be stored on the Compliance Management System.

# Wider certificates will be made available to contractors and in-house staff where required.

# SLHD will ensure that each property within its stock is inspected and issued with an Electrical Installation Condition Report to comply with current statutory legislation. Any defects or remedials found will have a classification coded C1, C2 or C3, definitions below.

All SLHD internal certificates are to be completed electronically and submitted on the agreed platform, and for the Electrical Team Leaders to Quality Supervisor check (QS), and counter sign.

All external certificates carried out by Contractors are to be completed electronically and QS by their internal Electrical assessor, counter signed and then sent to C365 for quality check and filing.

Defects

- Classification code C1: Danger present/ Risk of injury - Immediate remedial action should be undertaken to rectify the defect at the time of the inspection. If it is not possible for the electrician to complete the work and deem the electrical installation to be in a safe condition, the electrician should seek to isolate the parts of any circuit, which is deemed unsafe and raise a job to return and fully complete works within 28 days.

- Classification code C2 - Potentially dangerous. - Urgent remedial action should be undertaken. Where possible this will be done at the time of the inspection however if this is not possible the electrician should ensure a job is raised and is completed within 28 days.

- Classification code C3 - Improvement required. – These pose no risk to the electrical installation but are improvements that could be made to bring the installation in line with current standards. SLHD will ensure that all C3 faults are analysed using its certificate software system C365. Where trends and common faults are identified, these shall be considered as part of future electrical capital upgrade programmes.

If a customer refuses access repeatedly to their property, either for EICRs or for the Remedials Actions, the No Access Policy should be followed.

We ensure reasonable adjustments are made, provide appropriate support for tenants with vulnerabilities, and offer enhanced communication methods for customers with sensory impairments to promote equality throughout the EICR process. For further information please consult the Vulnerable Persons Policy.

# 5.3 SLHD has a range of measures in place to manage electrical safety within its

# properties. The below details all compliance activity,

# frequency of testing, and how the SLHD meets its statutory and regulatory

# obligations. This includes:

# Domestic Electrical Installation Condition Report.

# Non-domestic Electrical Installation Condition Report.

# Smoke detectors.

# Automatic doors, gates and barriers.

# Emergency lighting.

# Electrical Equipment Testing.

# Lightning protection.

# Fire Alarms

# Automatic Opening Vents (AOVs)

# Stock Condition Surveys

# 5.3.1 Smoke detectors

# As part of the annual gas safety check, EICR, at void stage or in a stock condition survey, the engineer will check smoke detectors and carbon monoxide alarms are working correctly. A new detector and/or alarm will be fitted if faulty or missing or a job raising for completion.

# 5.3.2 Automatic doors, barriers, and gates

# Automatic doors are checked and serviced Annually, and a certificate of safety provided by the specialist contractor confirming they meet British Standard EN 12453.

# 5.3.3 Emergency Lighting

# Emergency lighting systems are inspected monthly, and an annual 3-hour discharge safety inspection is completed. Once every 5 years, to conduct a system's photometric performance to ensure the light levels are in line with BS5266:2025, it is recommended to undertake this at the time of the EICR. Any defects found are repaired in line with BS5266:2025

# 5.3.4 Electrical Equipment Testing

# Any portable equipment (electrical equipment which does not form part of the fixed

# system is considered to be an electrical appliance). EET is undertaken by a

# competent person at intervals dependent upon level of risk. This includes items

# provide within furnished tenancies and in community centres. It does not apply to our customers own equipment. Appendix 1 details this further.

# Electrical equipment provided for furnished tenancies (White Goods), are to have an EET undertaken by SLHD, with a recommendation of further EET every 5 years in line with The Social Rented Sector Regulations 2025.

# 5.3.5 Lightning Protection

# Lightning Protection systems receive an annual safety inspection. Any defects found are repaired as required by a lightning specialist contractor in line with BS EN 62305

# 5.3.6 AOVs

# Automatic Opening Ventilation Systems to communal areas of buildings receive an annual safety inspection. Any defects found are repaired as required by external and internal service providers in line with BS7346-8 and/or manufacturer’s instructions.

# 5.3.7 Fire Alarms

# Fire Alarm Systems to building communal areas have an annual safety inspection undertaken. Any defects found are repaired as required by external and internal service providers in line with BS5839-1.

# 5.3.8 Stock Condition Surveys

# This is a further line of defence through stock condition surveys which will highlight any HHSRS cat 1 or cat 2 hazards with remedial actions raised to be completed within timescales.

# 5.4 Certification

# Modifications to existing systems, rewires, and new installations will be issued with an electrical test certificate, the type of which is determined by the nature of the work and may be:

# Electrical Installation Condition Report

# An Electrical Installation Certificate;

# A Fire Detection Certificate;

# An Emergency Lighting Certificate;

# A Minor Works Certificate.

# Domestic Ventilation Certificate

# Smoke Alarm Installation Certificate

# For any Notifiable Work stipulated under Part P undertaken to SLHD properties, the Electrical Team Leaders and any contractors will ensure a Building Regulations Compliance Certificate is issued within 30 days of completion of the work.

# All Certificates must be sent to the Electrical Compliance Officer in a timely manner and must be uploaded onto the Compliance Management System promptly.

# 6. 	Consultation

# 6.1 	The CDC Electrical Engineering Manager and the Electrical Safety and Standards Authorising Group (ESSAG) have been consulted about this policy.

# 6.2 	The Internal Service Provider (ISP) have been consulted about this policy.

# 6.3   One Voice Forum have been consulted.

# 7. 	Monitoring and Review

# 7.1 	This policy will be reviewed every three years for accuracy and will take into account any legislative changes or requirements.

# 7.2 	Monitoring of the policy will be through the safety and compliance framework and the results of the quality control inspections which are fed into the monthly electrical management meetings.

# 7.3 	The Electrical Registration held by SLHD requires external monitoring by NICEIC annually.

# 7.4 	The performance standards of compliance with Electrical Safe registration is monitored externally by NICEIC in addition to internal monitoring of compliance with Electrical Regulations.

# 8. Emergency Procedures

# 8.1 	For any emergency repairs please consult the Repairs and Maintenance Policy Sections 6.6.1.1 and 6.6.1.2.

# Examples of emergency repairs include;

# Exposed live cables.

# Accessories with thermal damage.

# No Power to Sockets or Lights.

# 8.2 	SLHD Repairs and Maintenance Team will relay any relevant Electrical Documentation to the Electrical Compliance Officer.

# 9.    Performance Standards

# 9.1 SLHD has a performance management framework detailing targets for Electrical Installation Condition Report work – including: -

# 99.67% of properties with a in date EICR as per set KPIs

# 100% of the annual programme visited

# 100% C2s completed within 28 days

# 100% of the number of properties with no valid EICR after the appropriate number of visits, to go through the legal proceedings to gain access via the No Access Team.

# 9.3 The monthly safety & compliance performance report is the governance and

# assurance reporting tool for stakeholders.

# 9.4 SLHD use Compliance Management system for driving the programme and for performance. This allows the Electrical Compliance Officer to proactively monitor, measure and report on compliance activities in real time.

# 10.	Partnership Issues

# 10.1 	The Mechanical and Electrical Service Manager will work closely in association with CDC’s Procurement Team and Electrical Compliance Officer on any contracts with a requirement for electrical works, will attend regular contract meetings with any contractor carrying out electrical works, ensure regular health and safety monitoring visits are carried out on contractors and SLHD electricians and work closely with all partners in relation to the development, monitoring and revision of all SLHD policies in relation to electrical works and safety.

# Appendix 1

# For definitions of Formal Visual and Combined Inspection & Test please refer to HSG107